## Integrations
Smart Building System Integration Matrix |  |  |  | Update 10-02-22 EJM | EXAMPLE - Modify for specific project
System | Specification Section/Furnished By | Protocol | Connection | Master Systems Integrator - Div. 25 | Control System Contractor - Div. 23 | Network Contractor | OwnerIT/Security | Division 26 Electrical Contractor | Approximate Integration Point Count | Approximate Graphic Page Count
OT Network (OTN) | Owner | TCP/IP | RJ-45 | Makes final connection to networked device, configures OTN |  | Install LAN, Cable, Switches , provide LAN drops with cable connector. Set up Firewalls, security, etc. . |  | Install LAN, Cable, Hubs, provide LAN drops with cable connector. | 500 | 10 Graphic Architecture Diagrams. Indicate health of each Niagara device. Link to Niagara Security Dashboard for each Jace, Ciper and NEWS.
NOC Servers, Printers, Furniture | Owner | TCP/IP | RJ-45 | Provide installation of displays and pc, keyboard etc. in console. Set up displays and browser connections as required. |  |  |  | Provide Power | NA | NA
Niagara Enterprise Web Supervisor Software | Division 25/MSI | TCP/IP | RJ-45 | Install software , program, connect |  |  |  |  | 10000 | See graphic requirements described per system.
JACE - 8000, VEC-10 | Division 25/MSI | FOXS | RJ-45 | Furnish, install, program, commission JACE, EDGE 10. Integrate Data from Jaces to NEWS. | Install, program, connect local controllers to JACE in cooperation with MSI |  |  | Provide Power | 30/VAV | 1 Graphic per local controller
Lighting Control | Division 26 Electrical | Appropriate open protocol | RJ-45 | Integrate Lighting data into NEWS. Program graphics. Integrate occupancy indications with local HVAC zones. Provide occupancy commands to JACE. |  |  |  | Furnish, install, program, connect to OT Network as directed. Expose lighting points to network, provide documentation to MSI | 1000 | Floor Plan Graphics. 1 Key system operational graphic with 25 points.
Electrical Switchgear and Generators | Division 26 Electrical | MODBUS RTU/TCP | RS-485/RJ-45 | Integrate Electrical data into Jace and NEWS. Provide MODBUS RS-485/RJ-45 port on Jace-8000 |  |  |  | Furnish, install, program, connect to OT Network. Expose Modbus points to network, provide documentation to MSI. | 500 | Provide electrical data graphics with roll ups of power by floor and building. Utilize Niagara Analytics for details of power rollups.
Fire Alarm System | Division 26 Electrical | BACnet IP | RJ-45 | Integrate Fire Alarm data into NEWS. Alarm, Trouble, Zone , and device indication |  |  |  | Furnish, install, program, connect to Base Building Network. Expose BACnet IP points to network, provide documentation to MSI | 1000 | Show data on all floor plan graphics. Add FA Panel graphic with 10 key operational parameters
Digital Signage System | TBD | TCP/IP | RJ-45 | Push necessary building data to Digital Signage System Server via API TBD |  |  |  |  | 50 | Provide one key graphic with key I points being pushed to Digital Signage System
Building DDC Controllers | Division 23/HVAC Controls Contractor | BACnet MSTP/IP | RS-485 | Furnish, install, program, commission JACE, EDGE 10. Integrate Data from Jaces to NEWS. | Install, program, connect local controllers to JACE in cooperation with MSI |  |  | Provide Power to control panels. | 2000 | Provide detailed graphics of application controllers and show each device on the floor plans.
Tenant Niagara VAV Controllers | Division 23/HVAC Controls Contractor | Niagara FOXs | RJ-45 | Integrate Data from Niagara VAV controllers to NEWS. | Install, program, connect local controllers to Network in cooperation with MSI |  |  | Provide Power to control panels. | 2000 | Provide detailed graphics of application controllers and show each device on the floor plans.
IAQ Monitoring System | Division 23 Controls Contractor. | Modbus RTU via JACE-8000 . | RS-485 | Furnish, install, program, commission JACE, Integrate Data from IAQ devices to Jaces to NEWS. | Furnish, Install, Program, Commission IAQ devices. Connect to local JACE, |  |  | Provide Line Voltage Power | 250 | Add IAQ data to each floor plan graphic as well as a dedicated system graphic with all key IAQ points on the Building Heath Graphic.
Tenant Submetering | Division 23 Controls Contractor. | Modbus TCP to local JACE/Edge 10 | RJ-45 | Furnish, install, program, commission JACE, EDGE 10. Integrate Data from Meters to Jaces to NEWS. | Furnish, Program, Commission smart meters . Connect into JACE/Edge 10S. Coordinate installation with Div. 26 contractor. |  |  | Install Meters under direction of Div. 23 Contractor | 5000 | Provide submeter graphics by floor with power and power quality data. Provide electrical data graphics with roll ups of power by floor and building. Utilize Niagara Analytics for details of power rollups.
User Experience Center Kiosks | Owner | TCP/IP | RJ-45 | Push necessary building data to User Experience system via database or API connectivity TBD. Coordinate with owner User Experience supplier
CRAC and VRF | Division 23 Mechanical | BACnet IP/MSTP | RJ-45/RS-485 | Integrate data from CRAC/VRF to JACE-8000 and to NEWS |  |  |  |  | 100 | Provide Graphic for each CRAC and VRF System
ERU /DOAS | Division 23 Mechanical | BACnet IP/MSTP | RJ-45/RJ-485 | Integrate data from ERU/DOAS to JACE-8000 to NEWS |  |  |  |  | 50 | Provide Graphic for ERU/DOAS
Parking System | Building Parking Contractor | TCP/IP | RJ-45 | Integrate parking data from parking system via Rest API |  |  |  |  | 750 | Provide parking availability data per floor. One visitor parking graphics per floor to show actual spaces with status for each parking space.
NOTES:
NEWS = Niagara Enterprise Web Supervisor
OTN = Operational Technology Network
NOC = Network Operations Center